Copyright 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238239 - UNIT HEATERS

This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include unit heaters may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

- GENERAL

      - RELATED DOCUMENTS

        - Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

      - SUMMARY

        - Section Includes:

          - Cabinet unit heaters with centrifugal fans and [hot-water] [steam] coils.

          - Propeller unit heaters with [hot-water] [steam] coils.

      - DEFINITIONS

Retain abbreviations that remain after this Section has been edited.

        - BAS:  Building automation system.

        - CWP:  Cold working pressure.

        - PTFE:  Polytetrafluoroethylene plastic.

        - TFE:  Tetrafluoroethylene plastic.

      - SUBMITTALS

        - Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories for each product indicated.

        - LEED Submittal:

          - Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment complies.

          - Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

        - Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Edit subparagraphs below to suit Project.

          - Plans, elevations, sections, and details.

          - Location and size of each field connection.

          - Details of anchorages and attachments to structure and to supported equipment.

          - Equipment schedules to include rated capacities, operating characteristics, furnished specialties, and accessories.

Retain subparagraph below for hydronic and steam cabinet unit heaters.

          - Location and arrangement of piping valves and specialties.

Retain first subparagraph below for cabinet unit heaters with integral controls; delete if control devices are specified in Division 23 Section "Instrumentation and Control for HVAC."

          - Location and arrangement of integral controls.

          - Wiring Diagrams:  Power, signal, and control wiring.

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

        - Coordination Drawings:  Floor plans, reflected ceiling plans, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs and associated subparagraphs below to suit Project.

          - Suspended ceiling components.

          - Structural members to which unit heaters will be attached.

          - Method of attaching hangers to building structure.

          - Size and location of initial access modules for acoustical tile.

          - Items penetrating finished ceiling, including the following:

            - Lighting fixtures.

            - Air outlets and inlets.

            - Speakers.

            - Sprinklers.

            - Access panels.

            - <Insert item.>

          - Perimeter moldings for exposed or partially exposed cabinets.

Retain first paragraph below if Contractor is responsible for field quality-control testing.

        - Field quality-control test reports.

        - Operation and Maintenance Data:  For unit heaters to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

          - Maintenance schedules and repair part lists for motors, coils, integral controls, and filters (where applicable).

        - Warranty:  2 Year manufacturer’s standard warranty from date of shipment.

      - QUALITY ASSURANCE

        - Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

        - ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EA 2 requires compliance with requirements in ASHRAE/IESNA 90.1-2004.

        - ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

        - Equipment manufacturer shall be ISO 9001:2008 certified.

      - COORDINATION

Edit paragraph below to delete or add types of construction that penetrate or are supported by ceilings.  Delete this Article if fan-coil units are wall or floor mounted.

        - Coordinate layout and installation of fan-coil units and mounting system components with other construction that penetrates or is supported by walls and partition assemblies.

Retain paragraph below for units with outdoor air.

        - Coordinate size and location of wall sleeves for outdoor-air intake.

      - WARRANTY

Delete this Article if remote condensing unit is not required.

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

Warranties vary among manufacturers from covering the whole unit for up to 4 years, to only the compressor for 5 to 10 years, or only the condenser coil for 5 years.  Extended special warranties are limited to units in the 1- to 5-ton (3.5- to 17.6-kW) range, and then are usually restricted to residential applications.

        - Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of units that fail in materials or workmanship within specified warranty period.

          - Failures include, but are not limited to, the following:

            - Motor failure.

            - Coil leak.

Verify available warranties and insert number in subparagraphs below.

          - Warranty Period:  Two [Three] [Ten] <Insert number> years from date of Shipment.

          - Warranty Period (Motor Only):  Two [Ten] <Insert number> years from date of Shipment.

          - Warranty Period (Coil Only):  Two <Insert number> years from date of Shipment.

      - EXTRA MATERIALS

Retain this Article for cabinet unit heaters with filters.  Extra materials may not be allowed for publicly funded projects.

        - Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

          - Cabinet Unit Heater Filters:  Furnish <Insert number> spare filters for each filter installed.

- PRODUCTS

      - MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles, or the Fan-Coil-Unit Schedule on Drawings, in which manufacturers and products, or manufacturers only, are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers," "Manufacturers," and "Basis-of-Design Product" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

        - In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

Retain paragraph above if fan-coil units are described in this Section; retain paragraph below if fan-coil units are scheduled on Drawings.  See sample schedule in the Evaluations.

        - In the Cabinet Unit Heater Schedule where titles below are column or row headings that introduce lists, the following requirements apply to product selection:

          - Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

          - Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

          - Basis-of-Design Product:  The design for each cabinet unit heater is based on the product named.  Subject to compliance with requirements, provide either the named product or a comparable product by one of the other manufacturers specified.

      - CABINET UNIT HEATERS

        - Basis-of-Design Product:  Zehnder Rittling or a comparable product by one of the following:

Retain paragraph above or below.  Retain "Available" in first paragraph below for nonproprietary and delete for semiproprietary specifications.  Coordinate with Part 2 "Manufacturers" Article.

        - Manufacturers:

Retain list of manufacturers below with either paragraph above.

          - Zehnder Rittling

        - Description:  Factory-packaged and -tested units rated according to ASHRAE 33 and UL 1995.

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.  Retain one of first three paragraphs and list of manufacturers below.  See Division 01 Section "Product Requirements."

Retain and edit one "Coil Section Insulation" Paragraph below.  Flexible elastomeric insulation and mineral-fiber insulation with a foil face are available from some manufacturers to reduce the number of glass or mineral fibers circulating through the air-conditioned space.

Retain paragraph and subparagraphs below for duct-liner-type, glass-fiber insulation.

        - Insulation:  [½” thick, 2 lb density matt-faced fiberglass] [½” thick foil faced fiberglass with scrim and taped edges to prevent any fibers from reaching the airstream] [½” thick elastomeric closed cell foam insulation] complying with ASTM C 1071 and attached with adhesive complying with ASTM C 916.

          - Fire-Hazard Classification:  Insulation and adhesive shall have a combined maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84 and UL 723.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

          - Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

          - Antimicrobial Performance Rating of 0, no observed growth, per ASTM G-21 and ASTM G-22.

        - Chassis:  20 gauge galvannealed steel where exposed to moisture.  [Floor-mounting units shall have leveling screws].

Retain paragraph and subparagraphs below for flexible elastomeric insulation.

Retain paragraph and subparagraphs below for surface, semirecessed, and fully recessed units.  Cabinet is not required for concealed units.  Coordinate custom-color requirements in paragraph below with sample submittal requirements.  Coordinate field painting with Division 09 painting Sections.

First option in two subparagraphs below, for thickness of 0.0528 inch (1.35 mm), is the equivalent of 16-gage steel; second option, for 0.0677 inch (1.7 mm), is the equivalent of 14-gage steel.

        - Cabinet:  16 gauge [14 gauge] steel with [factory baked epoxy powder prime coating, ready for field painting] [baked epoxy powder coating in manufacturer's standard paint color as selected by Architect] [baked epoxy powder coating in manufacturer's custom paint color as selected by Architect].

- Vertical Units:

            - Removable front panel, 16 gauge [14 gauge] steel, with [integral reverse stamped louvers] [baked epoxy powder coated aluminum double deflection] [architectural aluminum bar] discharge grille, channel-formed edges and ¼-turn tamper-proof allen-head cam fasteners.

            - [Provide a grille in the return air opening. (RF, RFI, RS, RSI).]

            - Louvered panel shall be supplied with two flush, hinged access doors with slotted cam-lock fasteners. [tamper-proof allen-head security quarter turn fasteners.] [tamper-proof Torx-head security quarter turn fasteners.]

          - Horizontal Units:

            - The front panel shall be hinged, 16 gauge [14 gauge] steel providing full swing through 90° including removable safety chain(s) to prevent the panel from swinging fully open accidentally.  Includes [integral reverse stamped louvers] [baked epoxy powder coated steel] [baked epoxy powder coated aluminum double deflection] discharge grille, channel-formed edges and ¼-turn allen-head [Torx-head] cam fasteners.

          - End pockets shall be no less than 8” [Extended end pockets shall be no less than 14”] in width, located on both sides of the unit.

          - Steel recessing flanges for recessing fan-coil units into wall or ceiling.

          - All concealed units shall have a minimum 1" duct collar on the discharge.

        - Outdoor-Air Wall Box:  Aluminum, rain-resistant louver and adjustable, telescoping box with bird screen.

          - Louver Configuration:  Horizontal, rain-resistant louver.

          - Louver Material: Aluminum

          - Bird Screen:  1/2-inch (13-mm) mesh screen on interior side of louver.

          - Decorative Grille:  On outside of intake.

          - Finish: [Baked epoxy powder coating], color as selected by Architect from manufacturer's [standard] [custom] colors.

        - Outdoor-Air Damper:  Galvanized-steel blades with edge seals; with manual [two-position motorized] operation.

        - Filters:  Minimum arresta nce according to ASHRAE 52.1, and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

Retain one or more of three subparagraphs below.  Indicate filter type in the Fan-Coil-Unit Schedule on Drawings.  2-inch- (50-mm-) thick washable foam is not available.  Retain third subparagraph if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

          - 1” Washable Aluminum Mesh:  70 percent arrestance and 2 MERV.

          - 1” Glass Fiber Throwaway:  80 percent arrestance and 4 MERV.

          - 1” Reinforced Non-woven Media Throwaway:  95 percent arrestance and 8 MERV.

        - Hydronic Coils:  Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.083 inch (2.1 mm), rated for a minimum working pressure of 300 psig (2067 kPa) and a maximum entering-water temperature of 220 deg F (104 deg C). Minimum copper tube thickness shall be 0.016”. Minimum fin thickness shall be 0.0045”. Lanced fins shall not be acceptable. Coils shall be circuited for counter flow to maximize unit efficiency. Coil casing shall be fabricated from galvanized steel [stainless steel].  Include manual air vent [automatic air vent] and drain valve.

        - Steam Coils:  Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.083 inch (2.1 mm), rated for a maximum working pressure of 15 psig (689 kPa).

        - Fan and Motor Board:  Constructed from 18 gauge galvannealed steel.

          - Fan:  Forward curved, double width, centrifugal; directly connected to motor.  galvanized-steel wheels and fan scrolls.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

          - Motor:  [Permanently lubricated, multispeed PSC] [Electronically commutated high-efficiency, programmable brushless DC motor]; resiliently mounted on motor board. Shaded pole motors are not acceptable. Single speed motors are not acceptable.   Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

          - Wiring Termination: [Connect motor to chassis wiring with plug connection.]

Some manufacturers do not provide electric-resistance heating coils in downflow configuration.

Retain first paragraph and applicable subparagraphs below to require factory-piping package.

        - Factory, Hydronic Piping Package:  ASTM B 88, Type L copper tube with wrought-copper fittings and soldered joints.  Label piping to indicate service inlet.  [Piping package will be shipped factory installed.]

Retain one or more of first four subparagraphs below.

          - [Two] [Three]-way, [two-position] [3-wire floating modulating] [proportional 0-10 VDC modulating] control valve for dual-temperature coil.

          - [Two] [Three]-way, [two-position] [3-wire floating modulating] [proportional 0-10 VDC modulating] control valve for chilled-water coil.

          - [Two] [Three]-way, [two-position] [3-wire floating modulating] [proportional 0-10 VDC modulating] control valve for heating coil.

          - [Provide high pressure close-off actuator for 2 or 3-way on/off control valve. Maximum close-off pressure is 75 PSIG.]

          - Two-Piece Ball Valves:  Forged brass body with full-port, chrome-plated brass ball; PTFE seats; and 600-psig (4140-kPa) minimum CWP rating and blowout-proof stem.

          - Calibrated-Orifice Balancing Valves:  Bronze body, ball type; 200-psig (1376-kPa) working pressure, 250-deg F (121-deg C) maximum operating temperature; with calibrated orifice or venturi, connections for portable differential pressure meter with integral seals, threaded ends, and equipped with a memory stop to retain set position.

          - Automatic Flow-Control Valve:  Brass or ferrous-metal body; 600-psig (4140-kPa) working pressure at 325 deg F (163 deg C), with removable, corrosion-resistant, tamperproof, self-cleaning spring-loaded flow cartridge; factory set to maintain constant indicated flow with plus or minus 5 percent over differential pressure range of 2 to 45 psig (13.8 to 310 kPa).

          - Y-Pattern Hydronic Strainers:  Forged brass body; 600-psig (4140-kPa) working pressure; with sweat connections and perforated stainless-steel basket.

          - Forged Brass Unions:  ASME B16.22.

        - Control devices and operational sequences are specified in Division 23 Sections "Instrumentation and Control for HVAC" and "Sequence of Operations for HVAC Controls."

        - Basic Unit Controls:

          - Control voltage transformer.

Verify control features with manufacturer.

          - [Wall-mounted] [Unit-mounted] thermostat with the following features:

            - Heat--off switch.

            - Fan on-auto switch.

Retain first subparagraph below if multispeed motors are specified.

            - Fan-speed switch.

            - Exposed set point.

            - Exposed indication.

            - Degree F indication.

          - [Wall-mounted] [Unit-mounted] temperature sensor.

          - Remote bulb return air thermostat mounted in the end pocket with remote bulb temperature sensor within the air stream, regulating room air temperature by measuring the return air temperature.  Adjustable setpoint dial included.

          - Line voltage aquastat, shipped loose for remote mounting on the incoming supply piping.  Adjustable setpoint dial included.

Retain first paragraph and subparagraphs below and coordinate with "Basic Unit Controls" Paragraph and subparagraphs above or with control devices specified in Division 23 Section "Instrumentation and Control for HVAC."

        - [DDC ]Terminal Controller: Factory mounted.

        - Electrical Connection:  Factory wire motors and controls for a single electrical connection.

          - [Provide a service disconnect switch to isolate power from the unit during maintenance.]

          - [Provide a manual motor starter to provide overload protection for the motor.]

          - [Provide a ground fault circuit interrupter (GFCI).]

          - [Provide a power supply cord to enable powering of unit from wall outlet.]

If Project has more than one type or configuration of heater, delete paragraph and subparagraphs below and schedule cabinet unit heaters on Drawings.

      - PROPELLER UNIT HEATERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

        - Basis-of-Design Product:  Zehnder Rittling or a comparable product by one of the following:

Retain paragraph above or below.  Retain "Available" in first paragraph below for nonproprietary and delete for semiproprietary specifications.  Coordinate with Part 2 "Manufacturers" Article.

        - Manufacturers:

Retain list of manufacturers below with either paragraph above.

          - Zehnder Rittling

        - Description:  An assembly including casing, coil, fan, and motor in [vertical] [and] [horizontal] discharge configuration with adjustable discharge louvers.

Retain paragraph below for electric unit heaters.

        - Comply with UL 2021.

Retain paragraph below for explosion-proof electric unit heaters.

        - Comply with UL 823.

        - Cabinet:  All units shall have panels fabricated of not less than 18 gauge cold rolled steel.

          - Horizontal Units:

            - Casing consists of top/back and side halves.  Both halves are joined on top and back with hex head screws.

            - Top casing is furnished with threaded hanger connections for suspension of unit.

            - Fan venturi is die-formed on back half.

            - Units shall be equipped with horizontal, individually adjustable louvers (RH).

            - [Vertical louvers for four-way air control shall be included.]

          - Vertical Units:

            - Casing includes top and bottom pieces joined by corners and additional hardware.

            - Top casing is furnished with threaded hanger connections for suspension of unit

            - Provide a [cone-jet] [truncone] [one-way louver] [two-way louver] [3-cone anemostat] [4-cone anemostat] to provide specific air throw pattern

            - [Provide a pipe hanging kit that allows the unit to be hung from threaded pipe in lieu of threaded hanger rod.]

        - Cabinet Finish:  All painted cabinet exterior panels shall be finished with a standard textured gray epoxy powder coat paint.

Retain first paragraph below to comply with LEED-NC Prerequisite EQ 1.

        - Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

        - General Coil Requirements:  Test and rate [hot-water] [steam] propeller unit heater coils according to ASHRAE 33.

Retain one of first eight paragraphs below.  First paragraph is standard coil construction for hot-water heating systems.  Next four paragraphs are for situations where higher pressure ratings are required or corrosion resistance is required for some fluids inside the coils.

        - Hot-Water/Steam Coil:  Designed for either two-pipe steam or hot water heating system.

          - Coils shall have ½” nominal diameter seamless copper tubes and shall be mechanically expanded to provide an efficient, permanent bond between the tube and integral collar of the aluminum fin.

          - Minimum copper tube thickness shall be 0.028”.

          - Fins shall be die-formed and have a high efficiency aluminum surface optimized for heat transfer, air pressure drop and carryover.

          - Minimum fin thickness shall be 0.010”.

          - Lanced fins shall not be acceptable.

          - Fins are continuous across width and depth of coil and are vertically oriented to resist collection of dirt and foreign particles.

          - Coils are of non-ferrous construction and serpentine design for RH-18 and RH-24.  All other units incorporate brazed steel header tubes.

          - RH-18 through RH-86 units have ¾” female threaded NPT, brass header connections while all other units have male threaded NPT connections.

          - All coils shall be tested at 275 PSIG air pressure under water, and rated for a maximum 220 PSIG water or 150 PSIG steam and 375°F.

          - Coils have CRN pressure vessel certification for Ontario and Quebec provinces.

First paragraph below is standard coil construction for steam heating systems.  Next two paragraphs are for situations where higher pressure ratings are required or corrosion resistance is required for some fluids inside the coils.

        - Fan:  Propeller type with non-conducting, spark-proof aluminum blade wheel with steel hub directly mounted on motor shaft in the fan venturi.

        - Fan Guard:  Shall be finger-proof, constructed of welded steel rod and finished with a standard black epoxy powder coat paint.  Units mounted below 8 feet from the floor must be equipped with an OSHA fan guard to meet ETL and OSHA requirements.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add paragraphs below to suit Project.

        - Fan Motors:  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

          - Motor Type:  Permanently lubricated, two-speed, permanent split capacitor, totally enclosed with automatic reset integral thermal overload protection (3-phase motors require field supplied motor overload protection), designed to handle up to 104°F maximum constant ambient temperature. Shaded pole motors are not acceptable. Single speed motors are not acceptable.  [Explosion proof motors have an enclosure designed and constructed to withstand an explosion of a specified gas or vapor which may occur within the motor and to prevent the ignition of this gas or vapor surrounding the unit.  Explosion proof motor is suitable for Class I, Div I&II, Groups C&D and Class II, Div I&II, Groups F&G.  The explosion proof motors may not be used with a fluid temperature in excess of 329°F and still maintain the explosion proof rating for NEC ignition temperature rating T3B for grain dust.  All explosion proof motors are shelf mounted.]

Delete first paragraph below if controls are part of control system specified in Division 23 Section "Instrumentation and Control for HVAC." See Evaluations for discussion on control schemes and energy efficiency.

        - Control Devices:

          - [Unit-mounted] [Wall-mounted] [solid state variable speed controller.].

          - [Unit-mounted] [Wall-mounted] thermostat.

          - [Provide an explosion proof wall thermostat, shipped loose for remote mounting.] [Provide a clear, plastic locking thermostat guard, shipped loose for remote mounting.]

If Project has more than one type or size, delete paragraph and subparagraphs below and schedule propeller unit heaters on Drawings.

        - Electrical Connection:  Factory wire motors and controls for a single electrical connection.

          - [Provide a service disconnect switch to isolate power from the unit during maintenance.]

          - [Provide a manual motor starter to provide overload protection for the motor.]

If Project has more than one type or configuration of heater, delete paragraph and subparagraphs below and schedule wall and ceiling heaters on Drawings.

- EXECUTION

      - EXAMINATION

        - Examine areas to receive unit heaters for compliance with requirements for installation tolerances and other conditions affecting performance.

        - Examine roughing-in for [piping and] electrical connections to verify actual locations before unit heater installation.

        - Proceed with installation only after unsatisfactory conditions have been corrected.

      - INSTALLATION

Retain first paragraph below for vertical, wall-mounting cabinet unit heaters with wall boxes and outdoor-air intake louvers.

        - Install wall boxes in finished wall assembly; seal and weatherproof.  Joint-sealant materials and applications are specified in Division 07 Section "Joint Sealants."

        - Install cabinet unit heaters to comply with NFPA 90A.

        - Install cabinet unit heaters and propeller unit heaters level and plumb.

        - Suspend cabinet unit heaters from structure with elastomeric hangers[ and seismic restraints].  Vibration isolators[ and seismic restraints] are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

        - Suspend propeller unit heaters from structure with all-thread hanger rods and [elastomeric hangers] [spring hangers] [spring hangers with vertical-limit stop].  Hanger rods and attachments to structure are specified in Division 23 Section "Hangers and Supports for HVAC Piping and Equipment." Vibration hangers are specified in Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

Retain first paragraph below if controls are provided by unit heater manufacturer.  To comply with requirements of the Americans with Disabilities Act, verify mounting height with authorities having jurisdiction.

        - Install wall-mounting thermostats and switch controls in electrical outlet boxes at heights to match lighting controls.  Verify location of thermostats and other exposed control sensors with Drawings and room details before installation.

        - Install new filters in each cabinet unit heater within two weeks of Substantial Completion.

      - CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

        - Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.

        - Install piping adjacent to machine to allow service and maintenance.

        - Connect piping to cabinet unit heater's factory, hot-water piping package.  Install the piping package if shipped loose.

Retain paragraph below for concealed cabinet unit heaters.  Coordinate duct installation requirements with Drawings and with requirements specified in Division 23 Sections "Metal Ducts," "Nonmetal Ducts," and "Air Duct Accessories."

        - Connect supply and return ducts to cabinet unit heaters with flexible duct connectors specified in Division 23 Section "Air Duct Accessories."

Retain paragraph below for cabinet unit heaters with either hot-water or steam coils.

        - Comply with safety requirements in UL 1995.

Retain paragraph below for hot-water propeller unit heaters and for cabinet unit heaters if factory piping package is not required.

        - Unless otherwise indicated, install union and gate or ball valve on supply-water connection and union and calibrated balancing valve on return-water connection of unit heater.  Hydronic specialties are specified in Division 23 Section "Hydronic Piping."

Retain first paragraph below for steam unit heaters.

        - Unless otherwise indicated, install union and gate or ball valve on steam-supply connection and union, strainer, steam trap, and gate or ball valve on condensate-return connection of unit heater.  Steam specialties are specified in Division 23 Section "Steam and Condensate Heating Piping."

        - Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

        - Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

      - FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

        - Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

        - Perform the following field tests and inspections and prepare test reports:

          - Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Retain first subparagraph below for units that have electric-resistance heating coils.

          - Test and adjust controls and safety devices.  Replace damaged and malfunctioning controls and equipment.

        - Remove and replace malfunctioning units and retest as specified above.

      - DEMONSTRATION

Delete this Article if factory-authorized service representative is not required.

        - Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain cabinet unit heaters or propeller unit heaters.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 238239