- Mechanical Specifications

- Convectors

General

The contractor shall furnish and install Rittling Convectors with required mounting components and accessories to meet size, capacity and characteristics as required on the Equipment Schedule or 
on the plans. Units shall be installed in a neat and workmanlike manner in accordance with specifications and manufacturer recommendations. All material shall be manufactured by 
Zehnder Rittling.

Heating Elements

The heating element is designed for either two-pipe steam or two-pipe hot water systems. The coil is manufactured using non-ferrous 1/2" nominal copper tubing and aluminum fins which are die cut with a thickness of no less than 0.010". The fins have integral collars, which provide maximum heat transfer between the tubes and the fins. The tubes are mechanically bonded to the fins to ensure permanent contact.

The entire fin assembly shall be encased in a heavy gauge galvanized steel frame with spacers locked at regular intervals to provide added protection to the finned element.

Headers are cast brass with 3/4" FNPT tapings. Standard configuration is supplied with both inlet and outlet connections facing downward. Optional reverse tapping is available with one connection facing upward and the other connection facing downward.

Assembled heating elements shall be hydrostatically tested to 1700 PSI prior to leaving the factory.

Cabinet Construction

Enclosures shall be of the size and style as shown on the plans. The cabinet fronts shall be manufactured from 12-gauge, 14-gauge, 16-gauge or 18-gauge standard. Pick one - cold rolled steel. Cabinet front shall be flanged on top and sides for added rigidity.  The cabinet shall be reinforced and braced where necessary to provide additional stiffness. The liners shall be manufactured from 12-gauge, 14-gauge, 16-gauge, 18-gauge or 2-gauge standard. Pick one - cold rolled steel. 18-gauge cold rolled steel heating element support brackets shall be spot welded to the inside ends of the liners. Heating element support brackets allow for pitch adjustments of up to 1¼" for return of condensation in steam systems and as required by piping arrangements. Cabinet fronts are to be attached to liners using Phillips head fasteners standard. [Tamper proof Spanner head fasteners] [Tamper proof Allen Head fasteners]

Convector shall be provided with an air inlet/air discharge configuration as listed below. Must specify for each unit.

- Louvered inlet and/or outlet that are die-formed to allow directional flow of air with the maximum amount of free open area. The louvered openings are fabricated to be “pencil proof.”

- Security perforated inlet/perforated outlet shall be provided with 1/8" diameter holes on 3/16" staggered centerlines. 3/16" diameter holes on 1/4" staggered centerlines is also available.

- Architectural grille inlet and/or outlet shall be a heavy-duty extruded aluminum bar grille with a deep etched clear anodized finish. The vanes of the continuous extrusion shall have a 
15-degree deflection for directional airflow. The grille opening shall be “pencil proof.”

- Arched inlet, available on SF, FL, RL and PL models, when an open inlet is required for floor mounted units. PL and RL models to be 3-sided overlap with this option.

Convector cabinets shall be provided with the following configurations:

- Type SF – This fully exposed floor convector has sloping outlet and is designed for mounting to a sidewall. The inlet air is directed through bottom front inlet. Louvered inlet and outlet as standard.

- Type FL – This fully exposed floor mounted convector is attached to the sidewall. The flat top design features front outlet and bottom front inlet. Louvered inlet and outlet as standard.

- Type SL – This fully exposed wall mounted convector with slope outlet. The inlet air is directed through the open bottom.

- Type WL – This fully exposed wall convector features a flat top with front vertical outlet. Inlet air passes through the open bottom.

- Type RL – This semi-recessed convector is designed for partially recessed wall mounting. The front inlet and outlet are advantageous where wall space is limited. The liner is recessed partially into the wall leaving the remaining front panel exposed. Louvered inlet and outlet as standard.

- Type PL – This convector is designed for full recess into the wall. The front inlet and outlet are advantageous where wall space is limited. The liner is recessed completely into the wall leaving only the front panel exposed. Louvered inlet and outlet as standard.

Finish

All enclosures and accessories shall be degreased and chemically phosphatized before application of a durable, attractive electrostatic epoxy powder coating. Color to be selected from standard Zehnder Rittling color chart.

Accessories and Options

- Dampers shall be provided where indicated. Damper blades shall be fabricated from 20-gauge cold rolled material painted to match enclosure color. Threaded damper screw and trunion shall provide positive operation of blade to provide variable heat output.  Solid plastic damper knobs attached to damper screw shall operate damper. Recessed security Allen head operators shall be used in secure areas as indicated. Security damper must be operated by use of a hex key.

- Access doors shall be flush mounted with doors hinged at the top and use a slotted fastener-standard. Tamper proof spanner head fasteners and tamper proof Allen head fasteners are optional.

- Convectors shall be provided with 1/2" thick faced fiberglass insulation on cabinet fronts, liners and sides for special applications.

- End pockets shall be installed when noted on drawings and schedules. End pockets shall be left end only, right end only or both ends. Pick one. When provided the heating element shall be shortened and vertical baffle with element support shall be provided between the end of the element and the end of the cabinet.  The end pocket length shall be 6" long or 8" long. Pick one.  Consult factory for custom end pocket requirements.

- Units shall be manufactured in accordance with conformance to ISO 9001:2008 standards.