- Mechanical Specifications

- Econo-Line and High Capacity Series

General

The contractor shall furnish and install Rittling Econo-Line and High Capacity Series Fin Tube Enclosure with required mounting components and accessories to meet size, capacity and characteristics as required on the Equipment Schedule or on the plans. Units shall be installed in a neat and workmanlike manner in accordance with specifications and manufacturer recommendations. All material shall be manufactured by Zehnder Rittling.

Heating Elements

Copper heating elements, as indicated on the plans, shall consist of aluminum fins not less than .016" thick with integral fin collars, which space the fins and provide good tube to fin surface contact, permanently bonded to copper seamless drawn tubing by mechanically expanding the copper tubing, to ensure durability and eliminate noise from loose fins, while assuring performance at specified catalog ratings. The ends of the tube shall be finished OD (male) on one end and finished ID (female swaged) on the other end as to allow the use of standard domestic copper fittings.  Elements will be provided from 1 ft to 12 ft lengths in 6" increments.

Enclosures

Econo-Line Enclosures shall be of the size and style as shown on the plans. Enclosures shall be manufactured from 14-gauge, 16-gauge or 18-gauge. Pick one - cold rolled steel. Enclosures will be provided in one piece from 1ft to 8 ft lengths in 6" increments. The upper portion of the enclosure will be secured in a hinge type manner by use of a full length back panel, while the lower portion of the enclosure will be secured in place by snapping the cover over the bottom of the element bracket.   Element sliders are also provided on the bottom of the fin tube to allow the element to expand during operation. Air discharge louvers will be of a “pencil proof” design. Where noted on drawings or schedules a urethane gasket shall be provided with the unit to form air seal at wall.

High Capacity Enclosures shall be of the size and style as shown on the plans. Enclosures shall be manufactured from 14-gauge, 16-gauge or 18-gauge. Pick one - cold rolled steel. Enclosures will be provided in one piece from 1ft to 8 ft lengths in 6" increments. The full back panel and top of the enclosure are manufactured in one piece. A friction pivot adjustable damper vane allows for 90-degree rotation to modulate heat output. The front cover snaps into place on the element brackets.  Element sliders are also provided on the bottom of the fin tube to allow the element to expand during operation.

Finish

All enclosures and accessories shall be degreased and chemically phosphatized before application of a durable, attractive electrostatic epoxy powder coating. Color to be selected from standard Zehnder Rittling color chart.

Accessories and Options

- The Econo-Line full back panel is manufactured from 20-gauge galvannealed steel. For rigidity, the top projection of the full back plate shall position the enclosure away from the wall so as to allow for installation or removal of enclosure without damage to wall.

- Econo-Line Enclosure dampers shall be provided where indicated. Damper blades shall be fabricated from 18-gauge galvanized material painted to match enclosure color. Threaded damper screw and trunion shall provide positive operation of blade to provide variable heat output.  Solid plastic damper knobs attached to damper screw shall operate damper.

- 16-gauge brackets snap into place on back/top panel and have predrilled holes to use as templates when drilling mounting holes in the back of the panel. The brackets and enclosure are nailed to the wall in a single operation. For the High Capacity Series, the brackets brace the top panel and support the finned tube, front panel and damper vane.

- Access doors shall be provided in 12" long access panels or in the enclosure where noted on plans. For the Econo-Line Series, the doors shall have an overall size of 4-1/2" x 6" and for the High Capacity Series, the doors shall have an overall size of 6" x 6".  The doors should be installed where flow control or shut off valves are located. Doors shall be hinged at the top and use a slotted fastener to operate.

- A variety of trim pieces may be used between ends of enclosures and walls on wall-to-wall installations (inside corners, outside corners, wall trims, end caps and removable access panels). Trims are overlapping style only. All trims will be manufactured from 18-gauge cold rolled steel.

- Units shall be manufactured in accordance with conformance to ISO 9001:2000 standards.