Copyright 2003 and 2005 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

SECTION 238219 - FAN COIL UNITS

This Section includes requirements for the LEED Rating System.  However, equipment specified in this Section may not qualify for LEED Rating System prerequisites and credits.  Verify with manufacturers that the requirements for prerequisites and credits can be met.  To achieve prerequisites and obtain credits, HVAC system design alternatives that do not include fan coil units may be required.

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect."  Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

This Section includes fan-coil units and accessories.

DEFINITIONS

Retain abbreviation that remains after this Section has been edited.

BAS:  Building automation system.

SUBMITTALS

First three paragraphs below are defined in Division 01 Section "Submittal Procedures" as "Action Submittals."

Product Data:  Include rated capacities, operating characteristics, furnished specialties, and accessories.

LEED Submittals:

Retain first subparagraph below for LEED-NC Credit EA 4; coordinate with requirements selected in Part 2 for refrigerants.

Product Data for Credit EA 4:  Documentation required by Credit EA 4 indicating that equipment complies.

Product Data for Prerequisite EQ 1:  Documentation indicating that units comply with ASHRAE 62.1-2004, Section 5 - "Systems and Equipment."

Shop Drawings:  Detail equipment assemblies and indicate dimensions, weights, loads, required clearances, method of field assembly, components, and location and size of each field connection.

Wiring Diagrams:  Power, signal, and control wiring.

Remaining paragraphs are defined in Division 01 Section "Submittal Procedures" as "Informational Submittals."

Retain first paragraph and subparagraphs below if Drawings do not include detailed plans or if Project involves unusual coordination requirements.

Coordination Drawings:  Floor plans, reflected ceiling plans, and other details, drawn to scale, on which the following items are shown and coordinated with each other, based on input from installers of the items involved:

Edit subparagraphs below to suit Project.

Structural members to which fan-coil units will be attached.

Method of attaching support hangers to building structure.

Perimeter moldings for exposed or partially exposed cabinets.

<Insert item.>

Retain paragraph and subparagraphs below if required by seismic criteria applicable to Project.  Coordinate with Division 23 Section "Vibration and Seismic Controls for HVAC Piping and Equipment."

Retain first paragraph below if Contractor is responsible for field quality-control testing.

Field quality-control test reports.

Operation and Maintenance Data:  For fan-coil units to include in emergency, operation, and maintenance manuals.  In addition to items specified in Division 01 Section "Operation and Maintenance Data," include the following:

Maintenance schedules and repair part lists for motors, coils, integral controls, and filters.

Warranty:  2 Year manufacturer’s standard warranty from date of shipment.

QUALITY ASSURANCE

Electrical Components, Devices, and Accessories:  Listed and labeled as defined in NFPA 70, Article 100, by a testing agency acceptable to authorities having jurisdiction, and marked for intended use.

LEED-NC Prerequisite EQ 1 requires compliance with requirements in ASHRAE 62.1-2004, including requirements for controls, surfaces in contact with the airstream, particulate and gaseous filtration, humidification and dehumidification, drain pan construction and connection, finned-tube coil selection and cleaning, and equipment access.  Verify, with manufacturers, availability of units with components and features that comply with these requirements.

ASHRAE Compliance:  Applicable requirements in ASHRAE 62.1-2004, Section 5 - "Systems and Equipment" and Section 7 - "Construction and Startup."

LEED-NC Prerequisite EA 2 requires minimum efficiency equal to requirements in ASHRAE/IESNA 90.1-2004.

ASHRAE/IESNA 90.1-2004 Compliance:  Applicable requirements in ASHRAE/IESNA 90.1-2004, Section 6 - "Heating, Ventilating, and Air-Conditioning."

Equipment manufacturer shall be ISO 9001:2008 certified.

Sound Quality:

300 CFM and 400 CFM nominal units shall meet NC-27 sound criteria on high speed per ARI Standard 350-2000.

800 CFM nominal units shall meet NC-35 sound criteria on high speed per ARI Standard 350-2000.

600 CFM and 1000 CFM nominal units shall meet NC-45 sound criteria on high speed per ARI Standard 350-2000.

1200 CFM nominal units shall meet NC-54 on high speed per ARI Standard 350-2000.

COORDINATION

Edit paragraph below to delete or add types of construction that penetrate or are supported by ceilings.  Delete this Article if fan-coil units are wall or floor mounted.

Coordinate layout and installation of fan-coil units and mounting system components with other construction that penetrates or is supported by walls and partition assemblies.

Retain paragraph below for units with outdoor air.

Coordinate size and location of wall sleeves for outdoor-air intake.

WARRANTY

Delete this Article if remote condensing unit is not required.

When warranties are required, verify with Owner's counsel that special warranties stated in this Article are not less than remedies available to Owner under prevailing local laws.  Coordinate with Division 01 Section "Product Requirements."

Warranties vary among manufacturers from covering the whole unit for up to 4 years, to only the compressor for 5 to 10 years, or only the condenser coil for 5 years.  Extended special warranties are limited to units in the 1- to 5-ton (3.5- to 17.6-kW) range, and then are usually restricted to residential applications.

Special Warranty:  Manufacturer's standard form in which manufacturer agrees to repair or replace components of units that fail in materials or workmanship within specified warranty period.

Failures include, but are not limited to, the following:

Motor failure.

Coil leak.

Verify available warranties and insert number in subparagraphs below.

Warranty Period:  Two [Three] [Ten] <Insert number> years from date of Shipment.

Warranty Period (Motor Only):  Two [Ten] <Insert number> years from date of Shipment.

Warranty Period (Coil Only):  Two <Insert number> years from date of Shipment.

EXTRA MATERIALS

Extra materials may not be allowed for publicly funded projects.

Furnish extra materials described below that match products installed and that are packaged with protective covering for storage and identified with labels describing contents.

Fan-Coil-Unit Filters:  Furnish <Insert number> spare filters for each filter installed.

Retain subparagraph below only for fan-coil units with belt-driven fans.

PRODUCTS

MANUFACTURERS

See Editing Instruction No. 1 in the Evaluations for cautions about naming manufacturers and products.

Edit this Article with other Part 2 articles, or the Fan-Coil-Unit Schedule on Drawings, in which manufacturers and products, or manufacturers only, are named.  See Division 01 Section "Product Requirements" for an explanation of the terms "Available Manufacturers," "Manufacturers," and "Basis-of-Design Product" and the effect these terms have on "Comparable Product" and "Product Substitution" requirements.

In other Part 2 articles where titles below introduce lists, the following requirements apply to product selection:

Retain paragraph above if fan-coil units are described in this Section; retain paragraph below if fan-coil units are scheduled on Drawings.  See sample schedule in the Evaluations.

In the Fan-Coil-Unit Schedule where titles below are column or row headings that introduce lists, the following requirements apply to product selection:

Available Manufacturers:  Subject to compliance with requirements, manufacturers offering products that may be incorporated into the Work include, but are not limited to, manufacturers specified.

Manufacturers:  Subject to compliance with requirements, provide products by one of the manufacturers specified.

Basis-of-Design Product:  The design for each fan-coil unit is based on the product named.  Subject to compliance with requirements, provide either the named product or a comparable product by one of the other manufacturers specified.

VERTICAL STACK FAN-COIL UNITS

Many additional features, which vary with each manufacturer, are available for this product.  Include all features for fan-coil units that are required for Project, and identify additional features for specific units in the Fan-Coil-Unit Schedule on Drawings.

Basis-of-Design Product:  Zehnder Rittling or a comparable product by one of the following:

Retain paragraph above or below.  Retain "Available" in first paragraph below for nonproprietary and delete for semiproprietary specifications.  Coordinate with Part 2 "Manufacturers" Article.

Manufacturers:

Retain list of manufacturers below with either paragraph above.

Zehnder Rittling

Description:  Factory-packaged and -tested units rated according to ARI 440, ASHRAE 33, and UL 1995.

Closed-cell insulation with foil or matt facing is provided by some manufacturers to reduce the possibility of fibers from glass-fiber insulation being introduced into the conditioned space.

        - Insulation:  ½” thick, 2 lb density matt-faced fiberglass [½” thick foil faced fiberglass with scrim and taped edges to prevent any fibers from reaching the airstream] [½” thick elastomeric closed cell foam insulation] complying with ASTM C 1071 and attached with mechanical fasteners.  Adhesive or glue will not be acceptable.

Fire-Hazard Classification:  Insulation and adhesive shall have a combined maximum flame-spread index of 25 and smoke-developed index of 50 when tested according to ASTM E 84 and UL 723.

Retain subparagraph below to comply with LEED-NC Prerequisite EQ 1.

Airstream Surfaces:  Surfaces in contact with the airstream shall comply with requirements in ASHRAE 62.1-2004.

Antimicrobial Performance Rating of 0, no observed growth, per ASTM G-21 and ASTM G-22.

Removable drain pans are an extra feature with some manufacturers.

LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004.

Main Drain Pan:  Primary condensate drain pans shall be single wall, [18 gauge, painted galvanized steel] [20 gauge, stainless steel] for corrosion resistance, externally insulated with elastomeric closed cell foam insulation meeting insulation specification above and shall extend under the entire coil section.  Drain pans shall be of one piece construction and be positively sloped in 2 directions for condensate removal.  An easily removable rubber p-trap shall be furnished, factory piped to the condensate drain riser, held in place by 2 compression clamps.  Fabricate pans and drain connections to comply with ASHRAE 62.1-2004.

[Drain pan to be easily removable by sliding out from c-channel and shall be fastened by no more than 2 screws.  Drain pan access that requires the removal of coils is not acceptable.]

[Provide a condensate level switch to prevent unit from operating if the drain becomes blocked.]

[Provide a condensate pump with GFCI to continuously remove up to 5.0 gph.]

Coordinate custom-color requirements in paragraph below with sample submittal requirements.  Coordinate field painting with Division 09 painting Sections.

Cabinet:  20 gauge galvanized steel. All unit panels shall have knockouts for supply air openings and riser slots to facilitate the field conversion of riser location and supply air grille location. All units shall be designed to have drywall applied directly to the unit surface.  Back-to-back units shall have model FVA and FVB units joined together by a nominal six-inch wall that contains the supply, return and condensate risers.  The FVB unit will have a 5/8" layer of type-X gypsum board mechanically fastened to the unit wall adjacent to the risers.  The riser penetrations in the partition wall will be sealed with a fire-retardant caulk.  [Where a one hour rating of the partition between the units is required, a second layer of type-X gypsum board shall be mechanically fastened to the FVA unit wall adjacent to the risers.  The riser penetrations in the partition walls will be sealed with a fire-retardant caulk.  The unit shall be fabricated in compliance with ANSI/UL-1479 Standard Test Method for Fire Tests of Through Penetration Fire Stops.]

[For units with multiple outlets, include a sheet metal baffle, insulated on 2 sides, inside the discharge plenum to break the sight lines between the two discharge outlets and to attenuate room noise that could be transmitted through the openings.]

[Supply air opening knockouts shall be factory sealed and left in place during shipping and staging at the job site.]

Front Panels:  Removable, 18 gauge [14 gauge] [16 gauge] steel, with integral reverse stamped louvers. [Provide an architectural aluminum double deflection discharge grille] with a [factory baked epoxy powder prime coating, ready for field painting] [baked epoxy powder coating in manufacturer's standard paint color as selected by Architect] [baked epoxy powder coating in manufacturer's custom paint color as selected by Architect].  Liquid coat paint shall not be acceptable. The front panel shall be attached with a single tamper-proof allen-head quarter turn fastener to allow for easy removal and access for service.

The front panel mounts within a frame that is flush with the wall.  A front panel that protrudes from the wall is not acceptable.

Discharge grilles:  Provide an architectural grade [double deflection] [single deflection] [double deflection opposed blade damper] aluminum discharge grille with baked epoxy powder coated finish.

Retain first subparagraph below for stack-type fan-coil unit.

Retain paragraph and subparagraphs below for fan-coil units with outdoor-air intake.

Outdoor-air dampers are furnished for wall-mounting, vertical, exposed units only.

Outdoor-Air Damper:  Galvanized-steel blades with edge seals; with manual [two-position motorized] operation.

Filters:  Minimum arrestance according to ASHRAE 52.1, and a minimum efficiency reporting value (MERV) according to ASHRAE 52.2.

Verify available filter types with manufacturer.  Indicate filter thickness in "Capacities and Characteristics" Paragraph or in the Fan-Coil-Unit Schedule on Drawings.

Retain one or more of three subparagraphs below.  Indicate filter type in the Fan-Coil-Unit Schedule on Drawings.  2-inch- (50-mm-) thick washable foam is not available.  Retain third subparagraph if applying for LEED certification.  LEED-NC Prerequisite EQ 1 requires compliance with ASHRAE 62.1-2004, which requires a MERV rating of 6 or higher.

1” Washable Aluminum Mesh:  70 percent arrestance and 2 MERV.

1” Glass Fiber Throwaway:  80 percent arrestance and 4 MERV.

1” Reinforced Non-woven Media Throwaway:  92 percent arrestance and 7 MERV.

Hydronic Coils:  Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.083 inch (2.1 mm), rated for a minimum working pressure of 300 psig (2067 kPa) and a maximum entering-water temperature of 220 deg F (104 deg C). Minimum copper tube thickness shall be 0.016”. Minimum fin thickness shall be 0.0045”. Lanced fins shall not be acceptable. Coils shall be circuited for counter flow to maximize unit efficiency. Coil casing shall be fabricated from galvanized steel [stainless steel].  Include manual air vent [automatic air vent] and drain valve.

Steam Coils:  Copper tube, with mechanically bonded aluminum fins spaced no closer than 0.083 inch (2.1 mm), rated for a minimum working pressure of 100 psig (689 kPa).

Electric-Resistance Heating Coils:  Finned tubular electric heating elements shall be constructed of nickel-plated steel fins spirally wound over a heating element, metallurgically bonded by furnace brazing with fuses for overcurrent protection and limit controls for high-temperature protection consisting of an automatic reset primary thermal limit safety switch and back-up secondary thermal limit safety device. All heaters shall be single stage.  Terminate elements in stainless-steel machine-staked terminals secured with stainless-steel hardware.

Fan and Motor Board:  Constructed from 18 gauge galvannealed steel, installed on a z-channel mounting frame for ease of sliding fan/motor deck in and out.  Each fan/motor assembly shall be fastened by no more than 1 screw.  The motor shall have a quick connect to allow service and removal without the need for tools.

Fan:  Forward curved, double width, centrifugal; directly connected to motor.  galvanized-steel wheels and fan scrolls.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Division 23 Section "Common Motor Requirements for HVAC Equipment." If different characteristics are required, add subparagraphs below to suit Project.

Motor:  Permanently lubricated, multispeed PSC motor [Electronically commutated high-efficiency, programmable brushless DC motor] totally enclosed, tap wound for 3-speed with automatic reset integral thermal overload protection; resiliently mounted on motor board.  Shaded pole motors are not acceptable. Single speed motors are not acceptable.  Prior to shipping, all motors shall be assembled, factory tested and installed in the unit.  Comply with requirements in Division 23 Section "Common Motor Requirements for HVAC Equipment."

Wiring Termination:  Connect motor to chassis wiring with plug connection.

Factory, Hydronic Piping Package:  ASTM B 88, Type L copper tube with wrought-copper fittings and brazed joints.  Label piping to indicate service inlet. [Piping package will be shipped factory installed.]

Retain first paragraph and applicable subparagraphs below to suit Project.  Delete if factory piping package is not required.

Retain one or more of first four subparagraphs below.

[Two] [Three]-way, [two-position] [3-wire floating modulating] [proportional 0-10 VDC modulating] control valve for dual-temperature coil.

[Two] [Three]-way, [two-position] [3-wire floating modulating] [proportional 0-10 VDC modulating] control valve for chilled-water coil.

[Two] [Three]-way, [two-position] [3-wire floating modulating] [proportional 0-10 VDC modulating] control valve for heating coil.

[Provide high pressure close-off actuator for 2 or 3-way on/off control valve. Maximum close-off pressure is 75 PSIG.]

Two-Piece Ball Valves:  Forged brass body with full-port, chrome-plated brass ball; PTFE seats; and 600-psig (4140-kPa) minimum CWP rating and blowout-proof stem.

Calibrated-Orifice Balancing Valves:  Bronze body, ball type; 200-psig (1376-kPa) working pressure, 250-deg F (121-deg C) maximum operating temperature; with calibrated orifice or venturi, connections for portable differential pressure meter with integral seals, threaded ends, and equipped with a memory stop to retain set position.

Automatic Flow-Control Valve:  Brass or ferrous-metal body; 600-psig (4140-kPa) working pressure at 325 deg F (163 deg C), with removable, corrosion-resistant, tamperproof, self-cleaning spring-loaded flow cartridge; factory set to maintain constant indicated flow with plus or minus 5 percent over differential pressure range of 2 to 45 psig (13.8 to 310 kPa).

Y-Pattern Hydronic Strainers:  Forged brass body; 600-psig (4140-kPa) working pressure; with sweat connections and perforated stainless-steel basket.

Forged Brass Unions:  ASME B16.22.

Risers:  ASTM B 88, Type M (ASTM B 88M Type C) [ASTM B 88, Type L (ASTM B 88M, Type B)] seamless copper pipe with 3” flared end, factory assembled to unit.  Slip couplings are not acceptable.  Risers shall be insulated with ½” [3/4”] closed cell foam insulation covering the entire riser.  Insulation shall conform to NFPA 90A and carry no more than a 25/50 Flame Spread and Smoke Developed Rating, per ASTM E-84 and UL 723.

Retain subparagraph below for stack-type units with hydronic coils.

Control devices and operational sequences are specified in Division 23 Sections "Instrumentation and Control for HVAC" and "Sequence of Operations for HVAC Controls."

Retain paragraph above and delete paragraph and subparagraphs below if controls are part of overall temperature-control system.

Basic Unit Controls:

Control voltage transformer.

Verify control features with manufacturer.

[Wall-mounting] [Unit-mounted] thermostat with the following features:

Heat-cool-off switch.

Fan on-auto switch.

Retain first subparagraph below if multispeed motors are specified.

Fan-speed switch.

[Manual] [Automatic] changeover.

Exposed set point.

Exposed indication.

Degree F indication.

[non-digital] [digital, programmable] [digital, non-programmable]

[Wall-mounting] [Unit-mounted] temperature sensor.

Retain first paragraph and subparagraphs below and coordinate with "Basic Unit Controls" Paragraph and subparagraphs above or with control devices specified in Division 23 Section "Instrumentation and Control for HVAC."

[DDC] Terminal Controller: Factory mounted.

Electrical Connection:  Factory wire motors and controls for a single electrical connection.

[Provide a service disconnect switch to isolate power from the unit during maintenance.]

[Provide a manual motor starter to provide overload protection for the motor.]

Retain first paragraph and applicable subparagraphs below to suit Project.  Delete if factory piping package is not required.

Retain paragraph above and delete first paragraph and subparagraphs below if controls are part of overall temperature-control system.

EXECUTION

EXAMINATION

Examine areas to receive fan-coil units for compliance with requirements for installation tolerances and other conditions affecting performance.

Examine roughing-in for piping and electrical connections to verify actual locations before fan-coil-unit installation.

Proceed with installation only after unsatisfactory conditions have been corrected.

INSTALLATION

Install fan-coil units level and plumb.

Install fan-coil units to comply with NFPA 90A.

Retain paragraph below for horizontal, suspended units.

Verify mounting height in first paragraph below with authorities having jurisdiction to comply with requirements of the Americans with Disabilities Act.

Verify locations of thermostats, humidistats, and other exposed control sensors with Drawings and room details before installation.  Install devices [48 inches (1220 mm)] [60 inches (1525 mm)] <Insert dimension> above finished floor.

Install new filters in each fan-coil unit within two weeks after Substantial Completion.

CONNECTIONS

Coordinate piping installations and specialty arrangements with schematics on Drawings and with requirements specified in piping systems.  If Drawings are explicit enough, these requirements may be reduced or omitted.

Piping installation requirements are specified in other Division 23 Sections.  Drawings indicate general arrangement of piping, fittings, and specialties.  Specific connection requirements are as follows:

Install piping adjacent to machine to allow service and maintenance.

Connect piping to fan-coil-unit factory hydronic piping package.  Install piping package if shipped loose.

Connect condensate drain to indirect waste.

Install condensate trap of adequate depth to seal against the pressure of fan.  Install cleanouts in piping at changes of direction.

Retain first paragraph below for ducted fan-coil units.  Coordinate duct installation requirements with Drawings and with requirements specified in Division 23 Sections "Metal Ducts," "Nonmetal Ducts," and "Air Duct Accessories."

Connect supply ducts from fan-coil units with flexible duct connectors specified in Division 23 Section "Air Duct Accessories." Comply with safety requirements in UL 1995 for duct connections.

Ground equipment according to Division 26 Section "Grounding and Bonding for Electrical Systems."

Connect wiring according to Division 26 Section "Low-Voltage Electrical Power Conductors and Cables."

FIELD QUALITY CONTROL

Retain first paragraph below to require a factory-authorized service representative to perform, or assist Contractor with, field inspections, tests, and adjustments.  Retain one of two options to suit Project; delete both to require only an inspection before field testing.

Manufacturer's Field Service:  Engage a factory-authorized service representative to inspect[, test, and adjust] field-assembled components and equipment installation, including connections[, and to assist in field testing].  Report results in writing.

Perform the following field tests and inspections and prepare test reports:

Retain subparagraphs below with last paragraph above.  Edit to suit Project.  Delete subparagraphs if testing will be performed by Owner-engaged testing and inspecting agency.

Operational Test:  After electrical circuitry has been energized, start units to confirm proper motor rotation and unit operation.

Delete first subparagraph below if units do not have electric heat.

Operate electric heating elements through each stage to verify proper operation and electrical connections.

Test and adjust controls and safety devices.  Replace damaged and malfunctioning controls and equipment.

Remove and replace malfunctioning units and retest as specified above.

DEMONSTRATION

Delete this Article if factory-authorized service representative is not required.

Engage a factory-authorized service representative to train Owner's maintenance personnel to adjust, operate, and maintain fan-coil units.  Refer to Division 01 Section "Demonstration and Training."

END OF SECTION 238219