# Mechanical Specifications

# Security Series

General

The contractor shall furnish and install Rittling Security Series Fin Tube Enclosure with required mounting components and accessories to meet size, capacity and characteristics as required on the Equipment Schedule or on the plans. Units shall be installed in a neat and workmanlike manner in accordance with specifications and manufacturer recommendations. All material shall be manufactured by Zehnder Rittling.

Heating Elements

- Steel heating elements, as indicated on the plans, shall consist of galvanized fins not less than .030" thick permanently bonded to high pressure tubing by mechanically expanding the steel tubing, to ensure durability and eliminate noise from loose fins, while assuring performance at specified catalog ratings. The ends of the steel tube shall be threaded to accept all domestic NPT threaded fittings. Elements will be provided from 1.5 ft to 10 ft lengths in 6" increments.

- Copper heating elements, as indicated on the plans, shall consist of aluminum fins not less than .016" thick with integral fin collars, which space the fins and provide good tube to fin surface contact, permanently bonded to copper seamless drawn tubing by mechanically expanding the copper tubing, to ensure durability and eliminate noise from loose fins, while assuring performance at specified catalog ratings. The ends of the tube shall be finished OD (male) on one end and finished ID (female swaged) on the other end as to allow the use of standard domestic copper fittings.  Elements will be provided from 1 ft to 12 ft lengths in 6" increments.

Enclosures

Enclosures shall be of the size and style as shown on the plans. Enclosures shall be manufactured from 12-guage, 14-gauge, 16-gauge. Pick one - cold rolled steel. All enclosures shall be reinforced with a (minimum of two) gussets welded at ends of each enclosure style. The joining of enclosure shall be accomplished by use of internal joggle joiners providing added rigidity and alignment with adjoining enclosures. Fully perforated and partially perforated configurations are available. As a standard, 1/8" diameter holes on 3/16" staggered centerlines will be used for all security enclosures.   Enclosures will be provided from 1 ft to 8 ft lengths in 6" increments.

The upper portion of the enclosure will be secured by use of an offset strip or full back panel, while the lower portion of the enclosure will be secured to the wall by a fastener supplied by others. 5/16" diameter holes are provided on the bottom of the enclosure.

Finish

All enclosures and accessories shall be degreased and chemically phosphatized before application of a durable, attractive electrostatic epoxy powder coating. Color to be selected from standard Zehnder Rittling color chart.

Accessories and Options

- Offset strip will be manufactured from 20-gauge galvannealed steel while the full back panels are manufactured from 18-gauge, 16-gauge or 14-gauge. Pick one - galvanized steel. Where noted on drawings or schedules a urethane gasket shall be provided with the unit to form air seal at wall.

- Second row brackets shall be die formed from 16-gauge galvanneal for rigidity. All brackets must provide for lengthwise movement of elements during expansion and contraction as well as aligning elements to prevent contact with walls or enclosure.

- Enclosure dampers shall be provided where indicated. Damper blades shall be fabricated from 18-gauge galvanized material painted to match enclosure color. A tamper proof, key operated damper assembly provided with an exclusive “anti-slip” damper rod.

- Access doors shall be provided in 12" long access panels or in the enclosure where noted on plans. The doors shall have an overall size of 6" x 6" as standard (size may vary as space becomes limited) and be installed where flow control or shut off valves are located. Doors shall be hinged at the top and use a recessed Allen head fastener to operate.

- A variety of trim pieces may be used between ends of enclosures and walls on wall-to-wall installations (inside corners, outside corners, wall trims, end caps and removable access panels).  All trims will be manufactured from 18-gauge, 16-gauge or 14-gauge. Pick one - cold rolled steel.

- Units shall be manufactured in accordance with conformance to ISO 9001:2000 standards.