# Mechanical Specifications

# Utility E-Series

General

The contractor shall furnish and install Rittling E-Series Fin Tube Enclosure with required mounting components and accessories to meet size, capacity and characteristics as required on the Equipment Schedule or on the plans. Units shall be installed in a neat and workmanlike manner in accordance with specifications and manufacturer recommendations. All material shall be manufactured by Zehnder Rittling.

Heating Elements

- Steel heating elements, as indicated on the plans, shall consist of galvanized fins not less than .030" thick permanently bonded to high pressure tubing by mechanically expanding the steel tubing, to ensure durability and eliminate noise from loose fins, while assuring performance at specified catalog ratings. The ends of the steel tube shall be threaded to accept all domestic NPT threaded fittings. Elements will be provided from 1.5 ft to 10 ft lengths in 6" increments.

- Copper heating elements, as indicated on the plans, shall consist of aluminum fins not less than .016" thick with integral fin collars, which space the fins and provide good tube to fin surface contact, permanently bonded to copper seamless drawn tubing by mechanically expanding the copper tubing, to ensure durability and eliminate noise from loose fins, while assuring performance at specified catalog ratings.  The ends of the tube shall be finished OD (male) on one end and finished ID (female swaged) on the other end as to allow the use of standard domestic copper fittings.  Elements will be provided from 1 ft to 12 ft lengths in 6" increments.

Enclosures

ETO enclosures shall be of the size and style as shown on the plans. Enclosures shall be manufactured from 14-gauge, 16-gauge or 18-gauge. Pick one - cold rolled steel. Enclosure is designed rest directly on the heating element. The joining of enclosure shall be accomplished by use of internal joggle joiners providing added rigidity and alignment with adjoining enclosures. No sheet metal screws or other fastening devices shall be visible. Enclosures will be provided from 1 ft to 8 ft lengths in 6" increments.

EXO enclosures shall be of the size and style as shown on the plans. Enclosures shall be manufactured from 16-gauge or 18-gauge. Pick one - expanded metal. Enclosure is designed to rest directly on the heating element. Edges of the enclosure to be hemmed to provide a rounded edge.  No sheet metal screws or other fastening devices shall be visible. Enclosures will be provided from 1 ft to 8 ft lengths in 6" increments.

ETL enclosures shall be of the size and style as shown on the plans. Enclosures shall be manufactured from 14-gauge, 16-gauge or 18-gauge. Pick one - cold rolled steel. The joining of enclosure shall be accomplished by use of internal joggle joiners providing added rigidity and alignment with adjoining enclosures. No sheet metal screws or other fastening devices shall be visible.  Enclosures will be provided from 1 ft to 8 ft lengths in 6" increments.

Finish

All enclosures and accessories shall be degreased and chemically phosphatized before application of a durable, attractive electrostatic epoxy powder coating. Color to be selected from standard Zehnder Rittling color chart.

Accessories and Options

- ETO/EXO hanger brackets shall be die formed for rigidity. The brackets are designed to support the heating element and the enclosure. Additional brackets are required for two or three row applications.

- ETL brackets must provide for lengthwise movement of elements during expansion and contraction as well as aligning elements to prevent contact with brackets or enclosure.  Brackets to be made of 3/16" steel with ¾" coupling for pedestal mounting. The pedestal mount includes a pipe nipple and floor flange, fasteners to secure the pedestal to the floor by others.

- Access doors shall be provided on ETL enclosure only where noted on plans. The doors shall have an overall size of 4" x 6" and be installed where flow control or shut off valves are located. Doors shall be hinged at the top and use a slotted fastener to operate. Recessed security Allen head operators shall be used in secure areas as indicated.

- A variety of trim pieces may be used between ends of enclosures and walls on wall-to-wall installations (inside corners, outside corners, wall trims and end caps). Trims may be overlapping or butt-type depending on the application. All trims will be manufactured from 18-gauge cold rolled steel.

- Units shall be manufactured in accordance with conformance to ISO 9001:2000 standards.