- Mechanical Specifications

- Vertical Hi-Stack Fan Coil Units

- Models FVH, FVM, FVS and FVA/FVB

General

Furnish and install Vertical Hi-Stack Fan Coil Units where indicated on the plans and in the specifications, with required mounting components and accessories. All units shall be capable of meeting or exceeding the scheduled capacities for cooling, heating and air delivery. Units shall be ETL certified for the United States and Canada in compliance with UL/ANSI Standard 1995 and CSA C22.2 No. 236-95, and be certified as complying with ARI Standard 440-2008.

Construction

All unit cabinet panels shall be fabricated of 20-gauge galvanized steel panels. All cabinet panels shall be insulated with ½" thick 2 lb density matt-faced fiberglass [½" thick foil faced fiberglass with scrim and taped edges to prevent any fibers from reaching the airstream] [½" thick elastomeric closed cell foam insulation]. Insulation shall conform to NFPA 90A for fire, smoke and melting, and comply with a 25/50 Flame Spread and Smoke Developed Index per ASTM E-84 or UL 723. Additionally, insulation shall comply with Antimicrobial Performance Rating of 0, no observed growth, per ASTM G-21.

All unit panels shall have knockouts for supply air openings and riser slots to facilitate the field conversion of riser location and supply air grille location.

All units shall be designed to have drywall applied directly to the unit surface.

- Option: Back-to-back units shall have model FVA and FVB units joined together by a nominal six-inch wall that contains the supply, return and condensate risers.

The FVB unit will have a 5/8" layer of type-X gypsum board mechanically fastened to the unit wall adjacent to the risers. The riser penetrations in the partition wall will be sealed with a fire-retardant caulk.

Where a one hour rating of the partition between the units is required, a second layer of type-X gypsum board shall be mechanically fastened to the FVA unit wall adjacent to the risers. The riser penetrations in the partition walls will be sealed with a fire-retardant caulk. The unit shall be fabricated in compliance with ANSI/UL-1479 Standard Test Method for Fire Tests of Through Penetration Fire Stops.

- Option: Supply air opening knockouts shall be factory sealed and left in place during shipping and staging at the job site.

The front access panel shall be fabricated of not less than 18-gauge [16-gauge] [14-gauge] cold rolled steel and include reverse stamped louvers, leaving a smooth exterior surface. [Provide an architectural aluminum double deflection discharge grille with a powder coated paint finish to match cabinet color. Liquid coat paint shall not be acceptable.] The front panel shall be attached with a single tamper-proof Allen-head quarter turn fastener to allow for easy removal and access for service.

The front panel mounts within a frame that is flush with the wall. A front panel that protrudes from the wall is not acceptable.

- Option: Provide an architectural grade double deflection [single deflection] [double deflection opposed blade damper] aluminum discharge grille.

#### Painted finish

All front return panels, mounting frames and supply air grilles shall be finished with a standard ivory epoxy powder coat paint. Optional colors can be selected from the Zehnder Rittling Color Chart. Liquid coat paint shall not be acceptable. Custom colors are also available with the submission of a color chip for color match.

Sound

Units shall have published sound power level data tested in accordance with ARI Standard 350-2000 for non-ducted units.

300 CFM and 400 CFM nominal units shall meet NC-27 sound criteria on high speed.

800 CFM nominal units shall meet NC-35 sound criteria on high speed.

600 CFM and 1000 CFM nominal units shall meet NC-45 sound criteria on high speed.

1200 CFM nominal units shall meet NC-54 on high speed.

- Option: For units with multiple outlets, include an sheet metal baffle, insulated on 2 sides, inside the discharge plenum to break the sight lines between the two discharge outlets and to attenuate room noise that could be transmitted through the openings.

Power

Units shall not exceed scheduled power consumption.

Fan and motor

Unit fan shall be dynamically balanced, forward curved, DWDI centrifugal type constructed of galvanized steel for corrosion resistance. Motors shall be permanent split-capacitor [electronically commutated high-efficiency, programmable brushless DC], totally enclosed, tap wound for 3-speed, permanently lubricated sleeve bearing, type with automatic reset integral thermal overload protection and resiliently mounted. High static motors are available for ducted applications. Shaded pole motors are not acceptable. Single speed motors are not acceptable. Prior to shipping, all motors shall be assembled, factory tested and installed in the unit

The fan/motor assembly shall be constructed of 18-gauge galvannealed steel and installed in a z-channel mounting frame for ease of sliding fan/motor deck in and out through the front panel. Each fan/motor assembly shall be fastened by no more than 1 screw. The motor shall have a quick connect to allow service and removal without the need for tools.

Drain pan

Primary condensate drain pans shall be single wall, 18-gauge epoxy powder coat painted, galvannealed steel for corrosion resistance and extend under the entire coil section. Drain pans shall be of one piece construction and be positively sloped in 2 directions for condensate removal. An easily removable rubber p-trap shall be furnished, factory piped to the condensate drain riser, held in place by 2 compression clamps.

The primary drain pan shall be externally insulated with elastomeric closed cell foam insulation. The insulation shall carry no more than a 25/50 Flame Spread and Smoke Developed Rating per ASTM E-84 and UL 723 and an Antimicrobial Performance Rating of 0, no observed growth, per ASTM G-21. Internally sprayed insulation will not be acceptable.

- Option: Provide a primary drain pan constructed entirely of 20-gauge stainless steel for superior corrosion resistance.

- Option: Drain pan to be easily removable by sliding out from c-channel and shall be fastened by no more than 2 screws. Drain pan access that requires the removal of coils is not acceptable.

- Option: Provide a condensate level switch to prevent unit from operating if the drain becomes blocked.

- Option: Provide a condensate pump with GFCI to continuously remove up to 5.0 gph.

Coils

All cooling and heating coils shall optimize rows to meet the specified capacity. Coils shall have ½" OD seamless copper tubes and shall be mechanically expanded to provide an efficient, permanent bond between the tube and aluminum fin. Minimum copper tube thickness shall be 0.016".

Fins shall have high efficiency aluminum surface optimized for heat transfer, air pressure drop and carryover. Minimum fin thickness shall be 0.0045". Lanced fins shall not be acceptable.

All coils shall be tested at 350 PSIG air pressure under water, and rated for a maximum 300 PSIG working pressure at 200°F. Coils shall be circuited for counter flow to maximize unit efficiency.

All water coils shall be designed to connect with ½" nominal pipe connections.

Coil casing shall be fabricated from galvanized steel [stainless steel].

Heating coils shall be furnished in the re-heat position.

Steam coils shall be standard single tube steam type suitable for temperatures above 35°F and 15 PSIG steam pressure.

All water coils shall be provided with a manual air vent [automatic air vent] fitting to allow for coil venting.

Filters

All units shall be furnished with a minimum 1" nominal glass fiber throwaway [1" pleated 
MERV 7] [1" cleanable aluminum mesh] filter. Filters shall be tight fitting to prevent air bypass.

Electrical

Units shall be furnished with single point power connection. All electrical terminations to be made at control board using spade connectors.

- Option: Provide 24 VAC fan relays with 40 VA transformer as integral part of control board. Fan relays designed to operate in conjunction with factory provided [field provided] 24 V thermostat. Fan relays designed to accept 120, 208, 230, or 277 V input power.

Relays shall operate with generic non-digital [digital, non-programmable] [digital, programmable] thermostat designed to control up to three independently energized fan speeds. Thermostat will be provided with wiring harness complete with quick connect and pre-wired to terminal blocks.

- Option: Provide a service disconnect switch to isolate power from the unit during maintenance.

- Option: Provide a manual motor starter to provide overload protection for the motor.

Primary internal wiring and testing shall be conducted at the factory. All units shall be shipped with wiring diagrams.

Electric heat

Furnish an electric resistance heating assembly as an integral part of the fan coil unit, with the heating capacity, voltage and kilowatts scheduled.

The heater and unit assembly shall be listed for zero clearance and meet all NEC requirements, and be ETL listed with the unit as an assembly in compliance with UL/ANSI Standard 1995.

All heating elements shall be finned tubular electric heating elements, constructed of nickel-plated steel fins spirally wound over a heating element, metallurgically bonded by furnace brazing. Coil terminals are constructed of nickel-plated steel with epoxy end seal. Electric heating elements shall be located in the reheat position and shall be non-accessible to room occupants.

Elements terminated with stainless-steel machine-staked terminals secured with stainless-steel hardware.

All heaters shall include over temperature protection consisting of an automatic reset primary thermal limit safety switch and back-up secondary thermal limit safety device. All heaters shall be single stage.

Separate fusing is provided for each element for overcurrent protection.

All internal wiring shall be rated for 105°C minimum.

Piping packages

Provide a standard factory assembled and mounted valve piping package to consist of a 2 or 3-way, on/off, motorized electric control valve and two ball isolation valves.

Control valves shall be piped normally closed to the coil. Control valves shall be wired to terminal blocks or unit mounted thermostat, when provided, through quick connects to allow service and replacement of valves. Maximum entering water temperature on the control valve shall be 200°F, and maximum operating pressure shall be 300 PSIG.

- Option: Piping packages shall include stainless steel braided hoses to allow for thermal expansion within the unit cabinet. The hose shall be EPDM inner lined and Kevlar® reinforced, with stainless steel FNPT swivels and/or fittings. The hoses shall be rated for a maximum 450 PSIG working pressure at 250°F, and shall conform to NFPA 90A and carry no more than a 25/50 Flame Spread and Smoke Developed Rating, per ASTM E-84 and UL 723.

- Option: Unions shall be provided to allow easy removal of piping package from unit without the need for brazing or cutting pipe.

- Option: Provide 3-wire floating point modulating control valve (fail-in-place), in lieu of standard 2-position control valve wIth factory assembled valve piping package.

- Option: Provide proportional 0-10 VDC modulating control valve, in lieu of standard 2-position control valve with factory assembled valve piping package.

- Option: Provide high pressure close-off actuator for 2 or 3-way on/off control valve. Maximum close-off pressure is 75 PSIG.

- Option: Provide an adjustable flow control device for each piping package.

- Option: Provide a fixed flow control device for each piping package.

- Option: Provide pressure-temperature ports (P/T) for each piping package to allow measurement across the coil.

Piping packages shall be completely factory assembled including interconnecting pipe and factory tested for leaks. The valve packages are to be located in a serviceable location over the coil and primary drain pan. Valves that are tucked down behind coil(s) are unacceptable.

Risers

Furnish chilled and hot water supply and return risers mounted to the unit. Risers shall be Type-M seamless copper tube and include 3" deep swaged connections at the top for connection to the unit above. Slip couplings are not acceptable.

- Option: Provide Type-L copper risers that meet or exceed the requirements stated above.

Risers shall be insulated with ½" closed cell foam insulation covering the entire riser. Insulation shall conform to NFPA 90A and carry no more than a 25/50 Flame Spread and Smoke Developed Rating, per ASTM E-84 and UL 723.

- Option: Provide ¾" closed cell foam insulation that meets or exceeds the requirements stated above.

Condensate drain risers shall be Type-M seamless copper tube and meet the requirements stated above.

- Option: Risers shall be factory fabricated, bundled, and tagged separate from the fan coil units, allowing for shipment and installation of risers prior to the fan coil units.

Outside air damper

Provide a manual [two position motorized] outside air single blade damper integral to the unit. 
[A synchronous motor interlocked with the fan shall open the outside air damper automatically when the fan starts. If there is a loss in power or the blower stops, the damper shall return to a closed position.]

Units shall be manufactured in accordance with ISO 9001:2008 standards established and maintained by Zehnder Rittling.